# Cooling Zone – HVAC Load Design Case Study

Condition

A manufacturing manager requires the development of a dedicated cooling zone for a new food processing facility. He seeking a support form Engineering team to design an efficient system that ensures a higher output without .

Input Data :

Product details:

Malt based food product (wheat-based with malted barley and sugar)

Food baking performed in the Hot room conditions , then need to cooldown to food  in cooling zone to make a phase transformations.

- Product Entry Condition to cooling zone

Food Temperature: 80°C

Moisture: ~2%

- Product Handling process :

When Food is under the Hot conditions (80Deg C) , products stage – Dry state with 2% Moisture conditions.  While cooling down the product we cant increase the Moisture % In Product.

- Food receipt in the Multiple Open trays – Food Spread in each tray – 3 Kg / Tray

- MOC of tray: Stainless Steel

- Tray dimensions: 800 mm × 1000 mm × 50 mm

- Throughput: 10 trays per minute

- Cooling Requirement:

Final temperature conditions of the food  – 40 Deg C

- Room Specifications:

- Size: 10 m × 20 m × 3 mtr Height

- Construction: 200 mm concrete brick walls

- Room inside equipment and Manpower

-10 motors (6 × 3 kW + 4 × 5 kW) – Working load 60% only

- 1 electrical panel installed inside the room .

- 10 operators

- Infiltration:

- Door opens for 30 seconds

- Door size: 1 m Wide × 2 m Height

- Environmental Conditions:

- Outside: 45°C

- Room: 25°C

- Utilities:

- We can supply Chilled Water to Air Handling Unit at 6 Deg Centigrade.

- AHU can be placed adjacent to the Cooling room as per the below Dia

Goal :

- Determine HVAC system type and capacity

- Calculate cooling load and chiller TR capacity.

- Type of Ducting system to Maintain the room conditions

-

Constraints

- Food Cooling cycle is Min – 10 Min and Should not cross – 12 Min .

- Food Moisture % should not increase